## Sheet1
Replacement of internal fire doors, installation of fire seals to fire doors and decoration of fire doors and associated works at The Guildhall, Pike Street, Liskeard, PL14 3JE.
Ref No. | Location | Description | Price (£)
D0/1 | Rear of Beddoe's | Replace door with FD30 flush finish painted timber door with new 3no. 100mm butt fire rated hinges with intumescent packers behind, fit new overhead AD:M compliant fire rated closer, fit new sound activated fire alarm linked magnetic holdback
D0/2 | Rear of Pengelley's | Replace door with FD30 flush finish painted timber door with new 3no. 100mm butt fire rated hinges with intumescent packers behind, fit 10mm fire & smoke intumescent strip to door edges, fit new overhead AD:M compliant fire rated closer.
D0/3 | Rear or treatment room | Replace door with FD30 flush finish painted timber door with new 3no. 100mm butt fire rated hinges with intumescent packers behind, fit 10mm fire & smoke intumescent strip to door edges, fit new overhead AD:M compliant fire rated closer.
D0/4 | Rear of DVD store | Cover door on both sides with timber 50x75mm stud wall faced with Gyproc Fireline skimmed & decorated to provide 60mins fire resistant partition.
D0/5 | Beddoes cold store | Replace door with FD30 flush finish painted timber door with new 3no. 100mm butt fire rated hinges with intumescent packers behind, fit new overhead AD:M compliant fire rated closer, fit new GEOFire Agripper sound activated magnetic holdback.
D1/1 | North stair west inner door | Replace door with FD60 flush finich painted timber door with 3no. 100mm butt fire rated hinges with intumescent packers behind, fit 20mm fire intumescent strip to door edges, fit new pabic bar & lever. Replace wall & underside stair plasterboard overdoor with 60min fire rated Gyproc Fireline skim & decorate.
D1/2 | North stair east inner door | Replace door with FD60 flush finich painted timber door with 3no. 100mm butt fire rated hinges with intumescent packers behind, fit 20mm fire intumescent strip to door edges, fit new pabic bar & lever. Cover fanlight on both sides with facing of Gyproc Fireline skimmed & decorated to provide 60min fire resistance. Replace wall & underside stair plasterboard overdoor with 60mm fire rated Gyproc Fireline skim & decorate.
D2/1 | Mid north stair utilities cupboard | Fire stop verical service void within cupboard with 120min fire rated insulation batt & mastic seals max. 25mm wide to perimeter.
D2/2 | Studio Winter north stair | Fit new 3no. 100mm butt fire rated hinges with intumescent packer behind, remove existing 10mm smoke seal to door edges fit 20mm fire & smoke intumenscent strip to door edges, check timber panels min. 10mm thick, decorate in Envirograf 60min fire rated paint.
D2/3 | Mid north stair south door | Fit new 3no. 100mm butt fire rated hinges with intumescent packer behind, remove existing 10mm smoke seal to door edges fit 20mm fire & smoke intumenscent strip to door edges, check timber panels min. 10mm thick, decorate in Envirograf 60min fire rated paint.
D2/4 | Electricity meter cupboard | Face rear of each existing cupboard door with 30min fire rated board, remove strip twist ctaches, make/fit/decorate new door to match for top left opening , mastic fire seal service holes in cupboard through wall/floor/ceiling.
D2/5 | Gym north west door | Fit new 3no. 100mm butt fire rated hinges with intumescent packer behind, remove existing 10mm smoke seal to door edges fit 20mm fire & smoke intumenscent strip to door edges, check timber panels min. 10mm thick, decorate in Envirograf 60min fire rated paint.
D2/6 | West stair top inner door | Replace door with G/O FD30 flush finich painted timber door with single vision panel with 3 no. 100mm butt fire rated hinges with intumescent packers behind & fit 10mm fire and smoke intumescent strip to door edges, fit new overhead AD:M comoliant fire rated closer.
D2/7 | Top of south stair | Replace pair of doors with G/O FD30 flush finish painted timber doors with new 3no. 100mm butt fire rated hinges with intumescent strip to door edges, fit new panic bars and levers. Cover fanlight on both sides with facing of Gyproc Fireline skimmed & decorated to provide 60min fire restistance.
D2/8 | South stairs | Fire stop atop metal grill within stairwell with 120min fire rated insulation batt & mastic seals max. 25mm wide to perimeter.
D3/1 | Balcony store room | Fit new 3no. 100mm butt fire rated hinges with intumescent packer behind, remove existing 10mm smoke seal to door edges fit 20mm fire & smoke intumenscent strip to door edges, check timber panels min. 10mm thick, decorate in Envirograf 60min fire rated paint.
Other costs e.g. contingency (please specifiy)
Total Sum (£)